## Reference
Ref in FRAGILITY DATASHEET_V0.xlsx | Final Ref | ARTICLES | Asset
3 | 1 | D3.01_Syner-G_RC_final | H | 31
6 | 2 | DEVELOPMENT OF EMPIRICALLY-BASED FRAGILITIES OF RESIDENTIAL damage in the 2011 missouri tornado
8 | 3 | Supparsi - Building damage characteristics based on surveyed data tsunami
9 | 4 | Vulnerability assessment for reinforced concrete buildings exposed to landslides
2 | 5 | A hybrid method for the vulnerability assessment of RC and URM buildings
7 | 6 | Cimellaro et al . - Seismic resilience of a hospital system
| 29 | Quantification of model uncertainty in debris flow vulnerability assessment
| 30 | A reliability assessment of physical vulnerability of reinforced concrete walls loaded by snow avalanches
| 31 | N.E. Khorasani, T. Gernay, M. Garlock. 2016. Fire fragility functions for community resilience assessment
1 | 7 | D3.03_SYNER-G_Fragility functions for electric power system elements | SubSt
4 | 8 | Probabilistic Risk Assessment of Infrastructure Networks Subjected to Hurricanes
5 | 9 | GNS science report - An Analysis of Tsunami Impacts to Lifelines
2 | 10 | University of washington - Determining the Damage State of the Electrical Distribution System Following an Earthquake
3 | 11 | World bank group - INCREASING INFRASTRUCTURE RESILIENCE BACKGROUND REPORT
2 | 12 | Probabilistic risk assessment of oil and gas infrastructures for seismic extreme events | Pipe
7 | 13 | Collocation Impacts on the Vulnerability of Lifelines During Earthquakes with Applictions to the Cajon Pass, California
8 | 28 | Seismic vulnerability of gas and liquid buried pipelines
2 | 14 | HAZUS MR4 - Technical manual - Multihazard Loss Estimation Methodology - Earthquake Model | Rafin
3 | 15 | Falcao - SEISMIC ASSESSMENT TO GAS AND OIL LIFELINES
2 | 14 | HAZUS MR4 - Technical manual - Multihazard Loss Estimation Methodology - Earthquake Model | Storage
3 | 15 | Falcao - SEISMIC ASSESSMENT TO GAS AND OIL LIFELINES
5 | 24 | Fragility Curves of storage tanks impacted by strong winds
7 | 25 | Fragility and Risk Assessment of Aboveground Storage Tanks Subjected to Concurrent Surge, Wave, and Wind Loads
Haz | 14 | HAZUS MR4 - Technical manual - Multihazard Loss Estimation Methodology - Earthquake Model | Transm
2 | 16 | Probabilistic Risk Assessment of Infrastructure Networks Subjected to Hurricanes
1 | 11 | World bank group - INCREASING INFRASTRUCTURE RESILIENCE BACKGROUND REPORT
Syn | 1 | D3.01_Syner-G_RC_final
1 | 11 | World bank group - INCREASING INFRASTRUCTURE RESILIENCE BACKGROUND REPORT | TPP
3 | 17 | Climate change and critical infrastructure - floods
2 | 18 | HAZARD ANALYSIS AND RISK ASSESSMENT IN THERMAL POWER PLANT
2 | 19 | 14WCEE - SEISMIC VULNERABILITY AND PRIORITIZATION RANKING OF DAMS IN CANADA | Hydro
1 | 11 | World bank group - INCREASING INFRASTRUCTURE RESILIENCE BACKGROUND REPORT
1 | 11 | World bank group - INCREASING INFRASTRUCTURE RESILIENCE BACKGROUND REPORT | Solar
2 | 20 | Testing of Connections to Improve Hurricane Resistance of Aluminum Strucures
2 | 21 | Seismic Fragility Analysis of Monopile Offshore Wind Turbines under Different Operational Conditions | Wind
4 | 22 | Response of a Wind Turbine Structure to strong ground motion and high velocity winds
1 | 11 | World bank group - INCREASING INFRASTRUCTURE RESILIENCE BACKGROUND REPORT | NPP
4 | 23 | Pujari et al . - Optimisation of IDA-based fragility curves.pdf
| 26 | World bank group - Stronger Power : Improving Power Sector Resilience to Natural Hazards
| 27 | World bank group - Resilience and Critical Power System Infrastructure_Lessons Learned from Natural Disasters and Future Research Needs

## Damage and Restoration
Asset | Sub-category |  | Slight | Moderate | Extensive | Complete | Ref.
HEALTH-CARE | Hospital | Damage -> | 5% | 20% | 45% | 80% | 5
|  | Service [%] - > | 6.25% | 25% | 56.25% | 100% | 5*
|  | Downtime [days] -> | 2 | 68 | 270 | 360 | 6
| Pharmaceutical | Damage -> | 5% | 20% | 45% | 80%
|  | Service [%] - > | 0% | 50% | 100% | 100%
|  | Downtime [days] -> | 2 | 68 | 270 | 360
ENERGY | Trasmission line | Damage -> | 4% | 12% | 50% | 80% | 14
|  | Service [%] - > | 0% | 50% | 100% | 100% | 14
|  | Downtime [days] -> | 5 | 7 | 30 |  | 11
| Substation | Damage -> | 4% | 12% | 50% | 80% | 10
|  | Service [%] - > | 0% | 50% | 100% | 100% | 11
|  | Downtime [days] -> | 1 | 3 | 7 | 30 | 11
| Pipeline | Damage -> | 2% | 14% | 38% | 75% | 13
|  | Service [%] - > | 2.667% | 18.67% | 50.67% | 100% | 13*
|  | Downtime [days] -> | 3 | 11 | 25 | 44 | 13
| Rafineries | Damage -> | 1% | 10% | 20% | 100% | 15
|  | Service [%] - > | 1% | 10% | 20% | 100% | 15*
|  | Downtime [days] -> | 1 | 10 | 50 | 415 | 14
| Storage plant | Damage -> | 0% | 1.5% | 6.5% | 100% | 15
|  | Service [%] - > | 0% | 1.5% | 6.5% | 100% | 15*
|  | Downtime [days] -> | 0 | 10 | 50 | 400 | 14
| Thermal power-plant | Damage -> | 5% | 12% | 43% | 80% | 18
|  | Service [%] - > | 0% | 50% | 100% | 100% | 18
|  | Downtime [days] -> | 0 | 25 | 100 |  | 11
| Hydroelectric power-plant | Damage -> | 5% | 20% | 45% | 80% | 19
|  | Service [%] - > | 0% | 50% | 100% | 100% | 18*
|  | Downtime [days] -> | 0 | 25 | 100 |  | 11
| Solar power-plant | Damage -> | 5% | 12% | 43% | 80% | 18*
|  | Service [%] - > | 0% | 50% | 100% | 100% | 18*
|  | Downtime [days] -> | 0 | 25 | 100 |  | 11*
| Wind power-plant | Damage -> | 5% | 12% | 43% | 80% | 18*
|  | Service [%] - > | 0% | 50% | 100% | 100% | 18*
|  | Downtime [days] -> | 0 | 25 | 100 |  | 11*
| Nuclear power-plant | Damage -> | 5% | 12% | 43% | 80% | 18*
|  | Service [%] - > | 0% | 50% | 100% | 100% | 18*
|  | Downtime [days] -> | 0 | 25 | 100 |  | 11*

## Seismic
[5 empty] | Mean values [g] |  |  |  | St. deviation
Asset | Sub-category |  |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
HEALTH-CARE | Hospital | Type | Storeys | Year of construction
|  | RC building | 1-3 | pre-1950 | 0.091 | 0.184 | 0.302 | 0.416 | 0.781 | 0.742 | 0.725 | 0.732 | 1 | Hospital Reinforced concrete pre-1950 less than 3 storeys
|  | RC building | 4-7 | pre-1950 | 0.024 | 0.146 | 0.235 | 0.285 | 0.965 | 0.688 | 0.666 | 0.667 | 1 | Hospital Reinforced concrete pre-1951 less than 7 storeys
|  | RC building | 8+ | pre-1950 | 0.066 | 0.193 | 0.367 | 1.24 | 0.735 | 0.663 | 0.635 | 0.635 | 1 | Hospital Reinforced concrete pre-1952 more than 8 storeys
|  | RC building | 1-3 | post-1950 | 0.118 | 0.288 | 1.669 | 2.168 | 0.752 | 0.707 | 0.703 | 0.696 | 1 | Hospital Reinforced concrete post-1950 less than 3 storeys
|  | RC building | 4-7 | post-1950 | 0.098 | 0.205 | 0.857 | 1.703 | 0.66 | 0.642 | 0.637 | 0.62 | 1 | Hospital Reinforced concrete post-1951 less than 7 storeys
|  | RC building | 8+ | post-1950 | 0.096 | 0.271 | 1.58 | 4.26 | 0.63 | 0.604 | 0.586 | 0.533 | 1 | Hospital Reinforced concrete post-1952 more than 8 storeys
| Pharmaceutical | Type | Typologies
|  | Precast concrete building | All |  | 0.269 | 0.332 | 0.411 | 0.472 | 0.454 | 0.494 | 0.595 | 0.591
ENERGY | Trasmission line | Type | Typologies | Codes
|  | Transmission line | Anchored | Seismic | 0.28 | 0.4 | 0.72 | 1.1 | 0.3 | 0.2 | 0.15 | 0.15 | 14 | Transmission & Distribution line Anchored
|  | Transmission line | Unanchored | Standard | 0.24 | 0.33 | 0.58 | 0.89 | 0.25 | 0.2 | 0.15 | 0.15 | 14 | Transmission & Distribution line Unanchored
| Substation | Type | Typologies | Dimension
|  | Electrical Substation | Anchored | < 150 kV | 0.15 | 0.29 | 0.45 | 0.9 | 0.7 | 0.55 | 0.45 | 0.45 | 7 | Substation Anchored less than 150 kV
|  | Electrical Substation | Anchored | 150-350 kV | 0.15 | 0.25 | 0.35 | 0.7 | 0.6 | 0.5 | 0.4 | 0.4 | 7 | Substation Anchored less than 300 kV
|  | Electrical Substation | Anchored | > 350 kV | 0.11 | 0.12 | 0.2 | 0.47 | 0.5 | 0.45 | 0.35 | 0.4 | 7 | Substation Anchored more than 300 kV
|  | Electrical Substation | Unanchored | < 150 kV | 0.13 | 0.26 | 0.34 | 0.74 | 0.65 | 0.5 | 0.4 | 0.4 | 7 | Substation Unanchored less than 150 kV
|  | Electrical Substation | Unanchored | 150-350 kV | 0.1 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 7 | Substation Unanchored less than 300 kV
|  | Electrical Substation | Unanchored | > 350 kV | 0.09 | 0.13 | 0.17 | 0.38 | 0.5 | 0.4 | 0.35 | 0.35 | 7 | Substation Unanchored more than 300 kV
| Pipeline | Type | Typologies
|  | Pipeline | All |  | 0.24785 | 0.38837 | 0.55545 | 0.78232 | 0.42334 | 0.33536 | 0.23633 | 0.14008 | 28 | Pipeline | Changed on 1st april
| Raphineries | Type | Typologies | Dimension
|  | Raphinery | Anchored | <100,000 barrels/day | 0.29 | 0.52 | 0.64 | 0.86 | 0.55 | 0.5 | 0.6 | 0.55 | 14 | Refinery Anchored less than 100 kbarrels/day
|  | Raphinery | Anchored | >100,000 barrels/day | 0.38 | 0.6 | 0.98 | 1.26 | 0.45 | 0.45 | 0.5 | 0.45 | 14 | Refinery Anchored more than 100 kbarrels/day
|  | Raphinery | Unanchored | <100,000 barrels/day | 0.13 | 0.27 | 0.43 | 0.68 | 0.5 | 0.5 | 0.6 | 0.55 | 14 | Refinery Unanchored less than 100 kbarrels/day
|  | Raphinery | Unanchored | >100,000 barrels/day | 0.17 | 0.32 | 0.68 | 1.04 | 0.4 | 0.45 | 0.5 | 0.45 | 14 | Refinery Unanchored more than 100 kbarrels/day
| Storage plant | Type | Typologies
|  | Storage | Anchored |  | 0.3 | 0.51 | 0.51 | 0.88 | 0.55 | 0.52 | 0.52 | 0.51 | 14 | Storage plant Anchored
|  | Storage | Unanchored |  | 0.12 | 0.23 | 0.41 | 0.69 | 0.55 | 0.55 | 0.53 | 0.51 | 14 | Storage plant Unanchored
| Thermal power-plant | Type | Typologies
|  | Thermal power plant | Anchored |  | 0.2 | 0.42 | 0.81 | 1.31 | 0.55 | 0.54 | 0.53 | 0.52 | 11 | Thermal power plant Anchored
|  | Thermal power plant | Unanchored |  | 0.08 | 0.17 | 0.37 | 0.6 | 0.67 | 0.57 | 0.55 | 0.55 | 11 | Thermal power plant Unanchored
| Hydroelectric power-plant | Type | Typologies
|  | Dam | Concrete |  | 0.23 | 0.35 | 0.81 | 1.2 | 0.26 | 0.26 | 0.11 | 0.2 | 19 | Hydroelectric power plant Concrete
|  | Dam | Earth/rockfill |  | 0.12 | 0.29 | 0.72 | 1.02 | 0.33 | 0.27 | 0.18 | 0.17 | 19 | Hydroelectric power plant Rockfill
| Solar power-plant | Type | Typologies | Codes
|  | Solar power plant | Enhanced | Seismic | 0.19 | 0.37 | 0.8 | 1.44 | 0.64 | 0.63 | 0.63 | 0.61 | 11 | Solar power plant Seismic
|  | Solar power plant | Typical | Standard | 0.14 | 0.21 | 0.51 | 0.95 | 0.65 | 0.63 | 0.62 | 0.62 | 11 | Solar power plant Standard
| Wind power-plant | Type | Typologies
|  | Wind power plant | All |  | 0.95 | 0.975 | 1 | 1.61 | 0.55 | 0.55 | 0.55 | 0.6 | 21 | Wind power plant
| Nuclear power-plant | Type | Typologies
|  | Nuclear power plant | All |  | 0.798 | 1.028 | 1.221 | 1.257 | 0.598 | 0.556 | 0.519 | 0.247 | 11 | Nuclear power plant

## Wind
|  |  |  | Mean values [m/s] |  |  |  | St. deviation
Asset | Sub-category |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
HEALTH CARE | Hospital | Type | Typologies
|  | RC building | All | 97.5144 | 112.1683 | 122.7316 | 190.5663 | 0.23 | 0.22 | 0.21 | 0.26 | 2 | Hospital Reinforced concrete
| Pharmaceutical | Type | Typologies
|  | Precast concrete building | All | 35.0965 | 41.3429 | 44.4471 | 47.6747 | 0.145 | 0.105 | 0.111 | 0.108
ENERGY | Trasmission line | Type | Typologies
|  | Transmission line | All | 24.5325 | 44.7012 | 73.6998 | 134.2898 | 0.17 | 0.22 | 0.4 | 0.6 | 14 | Transmission & Distribution line
| Substation | Type | Typologies
|  | Electrical Substation | All | 24.5325 | 44.7012 | 73.6998 | 134.2898 | 0.17 | 0.22 | 0.4 | 0.6 | 8 | Substation
| Pipeline | Type | Typologies
|  |  |  | / | / | / | / | / | / | / | / | / | Pipeline
| Rafineries | Type | Typologies
|  |  | <100,000 barrels/day | 27.7 | 32.58 | 35.02 | 37.6071 | 0.07 | 0.07 | 0.07 | 0.07 | 24* | Refinery less than 100 kbarrels/day | Added on 31th march
|  |  | >100,000 barrels/day | / | / | / | / | / | / | / | / | 24* | Refinery more than 100 kbarrels/day
| Storage plant | Type | Typologies
|  |  | fill <10% | 27.7 | 32.58 | 35.02 | 37.6071 | 0.07 | 0.07 | 0.07 | 0.07 | 24 | Storage plant less than 10% filled | Added on 31th march
|  |  | fill <30% | 56.52 | 66.48 | 71.46 | 76.7426 | 0.07 | 0.07 | 0.07 | 0.07 | 24 | Storage plant less than 30% filled
|  |  | fill >30% | / | / | / | / | / | / | / | / | 24 | Storage plant more than 30% filled
| Thermal power-plant | Type | Typologies
|  | Thermal power plant | All | 35.29 | 41.51 | 44.62 | 47.92 | 0.13 | 0.12 | 0.12 | 0.12 | 11 | Thermal power plant
| Hydroelectric power-plant | Type | Typologies
|  | Dam | All | / | / | / | / | / | / | / | / | 26 | Hydroelectric power plant
| Solar power-plant | Type | Typologies
|  | Solar power plant | All | 40.31 | 47.42 | 50.97 | 54.74 | 0.23 | 0.23 | 0.23 | 0.23 | 11 | Solar power plant
| Wind power-plant | Type | Typologies
|  | Wind power plant | All | 51.15 | 60.16 | 64.67 | 69.45 | 0.07 | 0.07 | 0.07 | 0.07 | 21 | Wind power plant
| Nuclear power-plant | Type | Typologies
|  | Nuclear power plant | All | / | / | / | / | / | / | / | / | 27 | Nuclear power plant

## Flood
[5 empty] | Mean values [m] |  |  |  | St. deviation
Asset | Sub-category |  |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
HEALTH CARE | Hospital | Type | Storeys
|  | RC building | 1 |  | 0.24 | 0.54 | 1.15 | 5.34 | 0.88 | 0.88 | 0.88 | 0.88 | 3 | Hospital Reinforced concrete 1 storey | Changed on 31th march
|  | RC building | 2 |  | 0.19 | 0.5 | 1.24 | 5.96 | 0.73 | 0.73 | 0.73 | 0.73 | 3 | Hospital Reinforced concrete 2 storeys
|  | RC building | 3+ |  | 0.17 | 0.48 | 1.13 | 10.6 | 0.77 | 0.77 | 0.77 | 0.77 | 3 | Hospital Reinforced concrete more than 3 storeys
| Pharmaceutical | Type | Storeys
|  | Precast concrete building | 1 |  | 0.24 | 0.54 | 1.15 | 5.34 | 0.88 | 0.88 | 0.88 | 0.88
|  | Precast concrete building | 2 |  | 0.19 | 0.5 | 1.24 | 5.96 | 0.73 | 0.73 | 0.73 | 0.73
|  | Precast concrete building | 3+ |  | 0.17 | 0.48 | 1.13 | 10.6 | 0.77 | 0.77 | 0.77 | 0.77
ENERGY | Trasmission line | Type | Typologies
|  | Transmission line | All |  | / | / | / | / | / | / | / | / | 26 | Transmission & Distribution line
| Substation | Type | Typologies
|  | Electrical Substation | All |  | 0.8 | 1.5 | 2.25 | 2.25 | 0.3 | 0.3 | 0.2 | 0.2 | 9 | Pipeline
| Pipeline | Type | Typologies
[5 empty] | / | / | / | / | / | / | / | / | / | Substation | Added on 31th march
| Rafineries | Type | Typologies | Impact
|  |  | <100,000 bbl/d | Wave | 0.76722 | 1.9168 | 3.899 | 3.899 | 0.42 | 0.42 | 0.42 | 0.42 | 25* | Refinery Flooding wave less than 100 kbarrels/day | Added on 31th march
|  |  | <100,000 bbl/d | No wave | 1.1189 | 2.7954 | 5.6862 | 5.6862 | 0.25 | 0.25 | 0.25 | 0.25 | 25* | Refinery No flooding wave less than 100 kbarrels/day
|  |  | >100,000 bbl/d |  | / | / | / | / | / | / | / | / |  | Refinery more than 100 kbarrels/day
| Storage plant | Type | Typologies | Impact
|  |  | fill <30% | Wave | 0.76722 | 1.9168 | 3.899 | 3.899 | 0.42 | 0.42 | 0.42 | 0.42 | 25 | Storage plant Flooding wave less than 30% filled | Added on 31th march
|  |  | fill <30% | No wave | 1.1189 | 2.7954 | 5.6862 | 5.6862 | 0.25 | 0.25 | 0.25 | 0.25 | 25 | Storage plant No flooding wave less than 30% filled
|  |  | fill >30% |  | / | / | / | / | / | / | / | / |  | Storage plant more than 30% filled
| Thermal power-plant | Type | Typologies
|  | Thermal power plant | All |  | 0.61 | 1.524 | 3.1 | 3.1 | 0.005 | 0.005 | 0.005 | 0.005 | 17 | Thermal power plant
| Hydroelectric power-plant | Type | Typologies
|  | Dam | All |  | / | / | / | / | / | / | / | / | 26 | Hydroelectric power plant
| Solar power-plant | Type | Typologies
|  | Solar power plant | All |  | 0.61 | 1.524 | 3.1 | 3.1 | 0.005 | 0.005 | 0.005 | 0.005 | 17* | Solar power plant
| Wind power-plant | Type | Typologies
|  | Wind power plant | All |  | / | / | / | / | / | / | / | / | 26 | Wind power plant
| Nuclear power-plant | Type | Typologies
|  | Nuclear power plant | All |  | 0.61 | 1.524 | 3.1 | 3.1 | 0.005 | 0.005 | 0.005 | 0.005 | 17* | Nuclear power plant

## Landslide
|  |  |  | Mean values [m |  |  |  | St. deviation | [7 empty] | 1.1137 |  | 1.3547 |  | 1.688 |  | 2.0224
Asset | Sub-category |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL |  | DS1 | 0.2666 | DS2 | 0.20274 | DS3 | 0.17626 | DS4 | 0.17311 |  | 0.0044047 |  | 0.0025655 |  | 0.0022437 |  | 0.0022004
HEALTH-CARE | Hospital | Type | Typologies | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RC building | All | 1.1137 | 1.3547 | 1.688 | 2.0224 | 0.2666 | 0.20274 | 0.17626 | 0.17311 | 29 | Bulding Reinforced concrete 1 storey | Added on 24th june | 0.24018 | 0.0041184 | 0.50859 | 0.0041184 | 0.80341 | 0.0041184 | 0.99702 | 0.0041184 | 4.3514e-09 | 1.6961e-05 | 6.7543e-07 | 1.6955e-05 | 1.2642e-05 | 1.6857e-05 | 2.1985e-05 | 1.678e-05
| Pharmaceutical | Type | Typologies | [11 empty] | 0.44699 | 0.023666 | 0.76381 | 0.023666 | 1.019 | 0.019756 | 1.2742 | 0.023666 | 0.00030818 | 0.00054557 | 0.0023546 | 0.00045416 | 0.002095 | 0.00031192 | 0.003811 | 0.0003942
|  | RC building | All | 1.1137 | 1.3547 | 1.688 | 2.0224 | 0.2666 | 0.20274 | 0.17626 | 0.17311 | 29 |  |  | 0.6362 | 0.058851 | 0.99262 | 0.092081 | 1.2214 | 0.06276 | 1.5118 | 0.074488 | 0.017852 | 0.0016809 | 0.062534 | 0.00087302 | 0.033211 | 0.00087314 | 0.046415 | 0.00078811
[15 empty] | 0.78581 | 0.12531 | 1.1422 | 0.21132 | 1.371 | 0.13509 | 1.6835 | 0.1605 | 0.095422 | 0.00089332 | 0.20007 | 0.00012664 | 0.119 | 0.00025877 | 0.14467 | 0.00025044
[15 empty] | 0.88701 | 0.19764 | 1.2786 | 0.36574 | 1.5427 | 0.29146 | 1.7979 | 0.2426 | 0.19665 | 9.797e-07 | 0.38784 | 0.0004885 | 0.3047 | 0.0001753 | 0.24832 | 3.2808e-05
[15 empty] | 0.95742 | 0.27778 | 1.3974 | 0.54558 | 1.7231 | 0.52994 | 1.8859 | 0.34033 | 0.2853 | 5.6574e-05 | 0.56091 | 0.00023508 | 0.5464 | 0.0002709 | 0.34322 | 8.3289e-06
[15 empty] | 1.0498 | 0.3892 | 1.5163 | 0.71955 | 1.8683 | 0.71759 | 1.9871 | 0.44198 | 0.41232 | 0.00053479 | 0.71081 | 7.6358e-05 | 0.71756 | 9.6411e-10 | 0.45949 | 0.0003068
[15 empty] | 1.2654 | 0.67654 | 1.6571 | 0.85247 | 2.0047 | 0.84856 | 2.0663 | 0.54167 | 0.68407 | 5.671e-05 | 0.83983 | 0.00015966 | 0.83533 | 0.00017508 | 0.54937 | 5.9263e-05
[15 empty] | 1.3798 | 0.79383 | 1.8419 | 0.94434 | 2.1323 | 0.91893 | 2.1675 | 0.65504 | 0.78923 | 2.1111e-05 | 0.93515 | 8.4421e-05 | 0.9075 | 0.00013057 | 0.65552 | 2.3037e-07
[15 empty] | 1.5118 | 0.89352 | 2.0575 | 0.98734 | 2.2907 | 0.96389 | 2.2819 | 0.76255 | 0.8742 | 0.00037315 | 0.98036 | 4.8725e-05 | 0.95837 | 3.0427e-05 | 0.75723 | 2.8337e-05
[15 empty] | 1.7099 | 0.95998 | 2.4843 | 1 | 2.5459 | 0.9893 | 2.4183 | 0.86224 | 0.9461 | 0.00019267 | 0.99861 | 1.9315e-06 | 0.99013 | 6.9775e-07 | 0.84915 | 0.00017131
[15 empty] | 1.9739 | 0.9893 | 3.2059 | 1 | 3.2103 | 1 | 2.5987 | 0.93652 | 0.98409 | 2.7109e-05 | 0.99999 | 1.1532e-10 | 0.99987 | 1.7594e-08 | 0.92625 | 0.00010545
[15 empty] | 2.3787 | 1 |  |  |  |  | 2.8363 | 0.97952 | 0.99779 | 4.8846e-06 |  |  |  |  | 0.97464 | 2.3858e-05
[15 empty] | 3.2103 | 1 |  |  |  |  | 3.2103 | 1 | 0.99996 | 1.2792e-09 |  |  |  |  | 0.9962 | 1.4435e-05

## Rockfall
|  |  |  | Mean values [m] |  |  |  | St. deviation
Asset | Sub-category |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
HEALTH - CARE | Hospital | Type | Ductility
|  | RC building |  | 0.049939 | 2.4172 | 2.4172 | 2.6997 | 0.049995 | 0.4474 | 0.4474 | 0.53169 | 4 | Bulding Reinforced concrete 1 storey | Added on 24th june
| Pharmaceutical | Type
|  | Precast concrete building |  | 0.049939 | 2.4172 | 2.4172 | 2.6997 | 0.049995 | 0.4474 | 0.4474 | 0.53169 | 4

## Avalanche
|  |  |  | Mean values [kPa] |  |  |  | St. deviation
Asset | Sub-category |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
HEALTH-CARE | Hospital | Type | Typologies
|  | RC building | All | 7.8425 | 29.3095 | 56.5472 | 80.3213 | 0.14475 | 0.086716 | 0.061421 | 0.093041 | 30 | Bulding Reinforced concrete 1 storey | Added on 13th July
| Pharmaceutical | Type | Typologies
|  | RC building | All | 7.8425 | 29.3095 | 56.5472 | 80.3213 | 0.14475 | 0.086716 | 0.061421 | 0.093041 | 30

## Wildfire
|  |  |  | Mean values [FII] |  |  |  | St. deviation
Asset | Sub-category |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
All | All | Type | Typologies
|  | All | All |  |  |  | 0.001 |  |  |  | 0.001 | - | All | Added on 30th of September

## Tech
|  |  |  | Mean values [kJ/m2] |  |  |  | St. deviation
Asset | Sub-category |  |  | Slight | Moderate | Extensive | Complete | Slight | Moderate | Extensive | Complete | Ref. | LABEL - WEB TOOL
All | All | Type | Typologies
|  | All | All |  |  |  | 1500 |  |  |  | 0.9 | 31 | Bulding Steel-frame | Added on 30th of September